## Cover
CYPRESS CREEK EPC, LLC
OCHOCO SOLAR FARM
115 TO 34.5 kV SUBSTATION
CONDUIT AND CABLE SCHEDULES
Prepared by: DAH
Checked by: EDR
App. by: BJM
2018-04-06
Revision | Description |  | Date
A | ISSUED FOR REVIEW |  | 2018-01-31
B | ISSUED FOR PERMITTING - DRAFT |  | 2018-02-23
C | ISSUED FOR REVIEW |  | 2018-04-11
PRELIMINARY
(NOT FOR
CONSTRUCTION)

## LEGEND AND NOTES
GENERAL NOTES:
1. ALL METALLIC JUNCTION BOXES, RACEWAYS, CABLE TRAYS, PANELS, AND ENCLOSURES SHALL BE BONDED TO THE SUBSTATION GROUND GRID.
2. ALL AC SERVICE NEUTRALS SHALL BE BONDED TO GROUND AT THE SERVICE PANEL AND AT THE POINT OF TERMINATION.
3. SECONDARIES FOR CURRENT TRANSFORMERS AND VOLTAGE TRANSFORMERS SHALL OBSERVE THE FOLLOWING COLOR CODE:
A - RED B - BLUE C - BLACK N - ORANGE
4. ALL AC BRANCH FEEDERS SHALL OBSERVE THE FOLLOWING COLOR CODE (COLOR TABLE E-1):
X - BLACK Y - RED N - WHITE G - GREEN
5. ALL DC BRANCH FEEDERS SHALL OBSERVE THE FOLLOWING COLOR CODE (COLOR TABLE E-2):
POSITIVE (+) - RED NEGATIVE (-) - BLACK
6. AC POWER SUPPLY AND CONTROL CABLES SHOULD NOT BE INCLUDED IN
THE SAME CONDUIT
7. CABLES PROVIDED AND INSTALLED BY GENERAL CONTRACTOR
8. PANEL VENDOR TO SUPPLY THE CABLES AND LABOR CONTRACTOR
TO INSTALL.
9. ABOVE GROUND CONDUIT (NOT SHOWN ON DRAWING)
| SB1 | SWITCHBOARD No.1
| T1 | TRANSFORMER No. 1
| F1 | FEEDER No. 1
| 52T1 | CIRCUIT BREAKER No. 1
| AC | AC SERVICE BREAKER PANEL
| DC | DC SERVICE BREAKER PANEL
8. AC POWER SUPPLY AND CONTROL CABLES SHOULD NOT BE INCLUDED IN THE SAME CONDUIT
9. CABLES PROVIDED AND INSTALLED ON SITE BY GENERAL CONTRACTOR

## Conduit Schedule
CONDUIT NO. | CABLES INCLUDED | CONDUIT SCHEDULE |  | CONDUIT SIZE/TYPE | REMARKS
|  | FROM | TO |  |  | Series
C001 | SPARE, 666 | 115 kV MAIN GOAB | TRENCH | 2"
C003 | 1001,1002 | 115 kV CIRCUIT BREAKER No.1 (52T1) | TRENCH | 2"
C004 | 1003, 1004 | 115 kV CIRCUIT BREAKER No.1 (52T1) | TRENCH | 2"
C005 | 1005, 1006, 1007 | 115 kV CIRCUIT BREAKER No.1 (52T1) | TRENCH | 2"
C006 | 1008 | 115 kV CIRCUIT BREAKER No.1 (52T1) | TRENCH | 2"
C007 | 1009 | 115 kV CIRCUIT BREAKER No.1 (52T1) | PACIFICORP INTERFACE CABINET | 2"
C011 | 1011, 1012 | TRANSFORMER No. 1 (T1) | TRENCH | 2"
C012 | 1013, 1014 | TRANSFORMER No. 1 (T1) | TRENCH | 2"
C013 | 1015 | TRANSFORMER No. 1 (T1) | TRENCH | 2"
C014 | 1016 | TRANSFORMER No. 1 (T1) | TRENCH | 2"
C015 | SPARE | TRANSFORMER No. 1 (T1) | TRENCH | 2"
C016 | SPARE | TRANSFORMER No. 1 (T1) | TRENCH | 2"
C026 | 1105, 1106 | SUMP PUMP (T1) | TRENCH | 2"
C027 | 1140 | SUMP PUMP (T1) | TRENCH | 2"
C030 | 1021, 1022 | FEEDER BREAKER No. 1 (52F1) | TRENCH | 2"
C031 | 1023, 1073 | FEEDER BREAKER No. 1 (52F1) | TRENCH | 2"
C032 | 1024 | FEEDER BREAKER No. 1 (52F1) | TRENCH | 2"
C033 | SPARE | FEEDER BREAKER No. 1 (52F1) | TRENCH | 2"
C080 | 1071 | 34.5kV BUS No. 1 VT's | 34.5kV BUS No. 1 VT's JUNCTION BOX (34.5VT) | 1" | NOTE 9.
C081 | 1072, 1073 | 34.5kV BUS No. 1 VT's JUNCTION BOX (34.5VT) | TRENCH | 2"
C082 | SPARE | 34.5kV BUS No. 1 VT's JUNCTION BOX (34.5VT) | TRENCH | 2"
C086 | 1101 | STATION SERVICE XFMR. No. 1 | S.S. XFMR No.1 DISCONNECT | 2" | NOTE 9.
C087 | 1102 | S.S. XFMR No.1 DISCONNECT | TRENCH | 2"
C099 | 1108 | 120 VAC RECEPTACLE No. 1 | TRENCH | 1"
C100 | 1114, 1132 | JCT BOX No. 1 | TRENCH | 2"
C101 | 1112, 1133 | JCT BOX No. 1 | FLOOD LIGHT No. 1 | 1" | NOTE 9.
C102 | 1113 | FLOOD LIGHT No. 1 | FLOOD LIGHT No. 2 | 1" | NOTE 9.
C103 | 1133 | FLOOD LIGHT No. 1 | AREA LIGHT No. 5 | 1" | NOTE 9.
C104 | 1111, 1114 | JCT BOX No. 2 | TRENCH | 2"
C105 | 1115 | JCT BOX No. 2 | FLOOD LIGHT No. 3 | 1" | NOTE 9.
C106 | 1116 | FLOOD LIGHT No. 3 | FLOOD LIGHT No. 4 | 1" | NOTE 9.
C107 | 1132, 1134 | JCT BOX No. 3 | TRENCH | 2"
C108 | 1131 | JCT BOX No. 3 | AREA LIGHT No. 6 | 1" | NOTE 9.
C109 | 1130, 1134 | JCT BOX No. 4 | TRENCH | 2"
C110 | 1135 | JCT BOX No. 4 | AREA LIGHT No. 7 | 1" | NOTE 9.
C125 | 1109 | LIGHT POLE No. 2 | TRENCH | 2"
C126 | 1110 | LIGHT POLE No. 2 | LIGHT POLE No. 1 | 2"
C130 |  | FEEDER CIRCUIT EXIT No. 1 PHASE A | FEEDER DUCT BANK | 4" | STUB UP & CAP OUTSIDE FENCE (CABLES BY OTHERS)
C131 |  | FEEDER CIRCUIT EXIT No. 1 PHASE B | FEEDER DUCT BANK | 4" | STUB UP & CAP OUTSIDE FENCE (CABLES BY OTHERS)
C132 |  | FEEDER CIRCUIT EXIT No. 1 PHASE C | FEEDER DUCT BANK | 4" | STUB UP & CAP OUTSIDE FENCE (CABLES BY OTHERS)
C200 | 1211 | PACIFICORP INTERFACE CABINET | PACIFICORP CONTROL BUILDING | 2"
C201 | 1212 | PACIFICORP INTERFACE CABINET | PACIFICORP CONTROL BUILDING | 2"
C202 | SPARE | PACIFICORP INTERFACE CABINET | PACIFICORP CONTROL BUILDING | 2"
C204 | 1231 | PACIFICORP INTERFACE CABINET (PACIFICORP ADSS) | PACIFICORP CONTROL BUILDING | 2"
C259 | 3242 | 115 kV VT PHASE A | 115 kV VT JUNCTION BOX (115VT) | 2"
C260 | 3243 | 115 kV VT PHASE B | 115 kV VT JUNCTION BOX (115VT) | 2"
C261 | 3240 | 115 kV VT JUNCTION BOX (115VT) | TRENCH | 2"
C262 | 3244 | 115 kV VT PHASE C | 115 kV VT JUNCTION BOX (115VT) | 2" | NOTE 9.
C263 | SPARE | 115 kV VT JUNCTION BOX (115VT) | TRENCH | 2"
C300 | 1084 | CAPACITOR BANK NO. 1 (C1) | CAP DISCONNECT | 4"
C301 | 1080, 1081 | CAPACITOR BANK NO. 1 JCT BOX | TRENCH | 2"
C302 | 1082, 1083, 1085 | CAPACITOR BANK NO. 1 JCT BOX | TRENCH | 2"
C320 | 4/0 | TRANSFORMER No. 1 (T1) | GROUND GRID | 2"
C321 | 4/0 | TRANSFORMER No. 1 (T1) | GROUND GRID | 2"
C324 | 4/0 | TRANSFORMER No. 1 (T1) | GROUND GRID | 2"
C325 | 4/0 | TRANSFORMER No. 1 (T1) | GROUND GRID | 2"
C350 | 1300 | TRENCH | LOCAL DISTRIBUTION POWER METER BREAKER | 2" | STUB UP & CAP OUTSIDE FENCE (CABLES BY OTHERS)
C351 | SPARE | TRENCH | LOCAL COMMUNICATION JUNCTION BOX | 2" | STUB UP & CAP OUTSIDE FENCE (CABLES BY OTHERS)
C352 | 1301 | LOCAL DISTRIBUTION POWER METER BREAKER | LOCAL DISTRIBUTION UTILITY TRANSFORMER | 2" | NOTE 9.

## Cable Schedule
CABLE NO. | CONDUIT NO. | FUNCTION | CABLE SCHEDULE |  | CABLE WIRE NO. & SIZE | REMARKS
|  |  | FROM | TO |  |  | Series
1001 | C003, TRAY, C001 | A.C. POWER SUPPLY | A.C. PANEL CKT. # 1/3 | HV CIRCUIT BREAKER No.52T1 | 4/C #6 | NOTE 4
1002 | C003, TRAY | D.C. POWER SUPPLY | D.C. PANEL CKT. # 1/3 | HV CIRCUIT BREAKER No.52T1 | 2-1/C #6 | NOTE 5
1003 | C004, TRAY | CONTROL & INDICATION | HV CIRCUIT BREAKER No.52T1 | SWITCHBOARD No. 1 | 12/C #10
1004 | C004, TRAY | CONTROL & INDICATION | HV CIRCUIT BREAKER No.52T1 | SWITCHBOARD No. 1 | 12/C #10
1005 | C005, TRAY | HV OVER CURRENT CT'S | HV CIRCUIT BREAKER No.52T1 | SWITCHBOARD No. 1 | 4/C #10 | NOTE 3
1006 | C005, TRAY | HV DIFFERENTIAL CT'S | HV CIRCUIT BREAKER No.52T1 | SWITCHBOARD No. 1 | 4/C #10 | NOTE 3
1007 | C005, TRAY | SCADA | HV CIRCUIT BREAKER No.52T1 | SWITCHBOARD No. 1 | LST6
1008 | C006, TRAY | POWER METERING | HV CIRCUIT BREAKER No.52T1 | SWITCHBOARD No. 1 | 4/C #10 | NOTE 3
1009 | C007 | PACIFIC INTERFACE (CT'S) | HV CIRCUIT BREAKER No.52T1 | UTILITY INTERFACE CABINET | 4/C #6 | NOTE 3
1011 | C011, TRAY | A.C. POWER SUPPLY | A.C. PANEL CKT. # 5/7 | TRANSFORMER No. 1 | 4/C #6 | NOTE 4
1012 | C011, TRAY | D.C. POWER SUPPLY | D.C. PANEL CKT. # 5/7 | TRANSFORMER No. 1 | 2/C #10 | NOTE 5
1013 | C012, TRAY | MV DIFFERENTIAL CT'S | TRANSFORMER No. 1 | SWITCHBOARD No. 1 | 4/C #10 | NOTE 3
1014 | C012, TRAY | XO CT | TRANSFORMER No. 1 | SWITCHBOARD No. 1 | 4/C #10 | NOTE 3
1015 | C013, TRAY | TRIP AND ALARMS | TRANSFORMER No. 1 | SWITCHBOARD No. 1 | 12/C #10
1016 | C014, TRAY | SCADA | TRANSFORMER No. 1 | SWITCHBOARD No. 1 | LST6
1021 | C030, TRAY | A.C. POWER SUPPLY | A.C. PANEL CKT. # 11/13 | FEEDER BREAKER No. F1 | 4/C #10 | NOTE 4
1022 | C030, TRAY | D.C. POWER SUPPLY | D.C. PANEL CKT. # 13/15 | FEEDER BREAKER No. F1 | 2/C #10 | NOTE 5
1023 | C031, TRAY | CONTROL & INDICATION | FEEDER BREAKER No. F1 | SWITCHBOARD No. 1 | 12/C #10
1024 | C032, TRAY | SCADA | FEEDER BREAKER No. F1 | SWITCHBOARD No. 1 | LST6
1071 | C080 | MV BUS No. 1 POTENTIAL | MV BUS No. 1 V.T.'S | V.T. JUNCTION BOX No. 1 | 6-1/C #10 | NOTE 3
1072 | C081, TRAY | MV BUS No. 1 POTENTIAL | V.T. JUNCTION BOX No. 1 | SWITCHBOARD No. 1 | 4/C #10 | NOTE 3
1073 | C031, C081 | MV BUS No. 1 POTENTIAL | V.T. JUNCTION BOX No. 1 | FEEDER BREAKER No. F1 | 4/C #10 | NOTE 3
1080 | C301, KANYE | A.C. POWER SUPPLY | CAPACITOR BANK NO. 1 JCT BOX | A.C. PANEL No. 1 CKT. # 2 | 4/C #10 | NOTE 4
1081 | C301 | D.C. POWER SUPPLY (CONTROL) | CAPACITOR BANK NO. 1 JCT BOX | D.C. PANEL No. 1 CKT. # 2/4 | 2/C #10 | NOTE 5
1082 | C302 | CAP BANK NEUTRAL POTENTIAL | CAPACITOR BANK NO. 1 JCT BOX | SWITCHBOARD No. 1 | 4/C #10 | NOTE 3
1083 | C302 | CONTROL & INDICATION | CAPACITOR BANK NO. 1 JCT BOX | SWITCHBOARD No. 1 | 4/C #10 | NOTE 5
1084 | C300 | CAPACITOR BANK EXIT | CAPACITOR BANK NO. 1 | FEEDER BREAKER NO. F1 BUS | 3-2/0 AL 35 KV EPR | NOTE 5
1085 | C302 | CONTROL & INDICATION | CAPACITOR BANK NO. 1 JCT BOX | SWITCHBOARD No. 1 | 4/C #10 | NOTE 5
1100 |  | A.C. POWER SUPPLY | AUTOMATIC TRANSFER SWITCH No. 1 | A.C. PANEL MAIN | 3-1/C 2/0 | BY BUILDING MANUFACTURER
1101 | C086 | STATION SERVICE | STATION SERVICE XFMR. No. 1 | S.S. XFMR. No. 1 DISCONNECT | 3-1/C 2/0
1102 | C087, TRAY | STATION SERVICE | S.S. XFMR. No. 1 DISCONNECT | AUTOMATIC TRANSFER SWITCH No. 1 | 3/C-3/0 SER w/ 1/0 GRD
1103 | TRAY | A.C. POWER SUPPLY | A.C. PANEL CKT. # 9 | SWITCHBOARD No. 1 | 4/C #10 | NOTE 4
1105 | C026, TRAY | A.C. POWER SUPPLY | A.C. PANEL CKT. # 29 | TRANSFORMER 1 SUMP PUMP | 4/C #10 | NOTE 4
1106 | C026, TRAY | A.C. POWER SUPPLY | A.C. PANEL CKT. # 31 | XFMR 1 SUMP PUMP ALARMS | 4/C #10 | NOTE 4
1108 | C099, TRAY | A.C. POWER SUPPLY | A.C. PANEL CKT. # 26 | 120 VAC RECEPTACLE No.1 | 4/C #10 | NOTE 4
1109 | C125, TRAY | A.C. POWER SUPPLY | A.C. PANEL CKT. # 19 | LIGHT POLE No. 1 | 4/C #10 | NOTE 4
1110 | C126, TRAY | A.C. POWER SUPPLY | LIGHT POLE No. 1 | LIGHT POLE No. 2 | 4/C #10 | NOTE 4
1111 | C104, TRAY | A.C. POWER SUPPLY, FLOOD LTS | A.C. PANEL CKT. # 21 | JCT BOX No. 1 | 4/C #10 | NOTE 4
1112 | C101 | A.C. POWER SUPPLY, FLOOD LT | JCT BOX No. 1 | FLOOD LIGHT No. 1 | 4/C #10 | NOTE 4
1113 | C102 | A.C. POWER SUPPLY, FLOOD LT | FLOOD LIGHT No. 1 | FLOOD LIGHT No. 2 | 4/C #10 | NOTE 4
1114 | C100,C104 | A.C. POWER SUPPLY, FLOOD LT | JCT BOX No. 1 | JCT BOX No. 2 | 4/C #10 | NOTE 4
1115 | C105 | A.C. POWER SUPPLY, FLOOD LT | JCT BOX No. 2 | FLOOD LIGHT No. 3 | 4/C #10 | NOTE 4
1116 | C106 | A.C. POWER SUPPLY, FLOOD LT | FLOOD LIGHT No. 3 | FLOOD LIGHT No. 4 | 4/C #10 | NOTE 4
1130 | C109 | A.C. POWER SUPPLY, AREA LT | A.C. PANEL CKT. # 23 | JCT BOX No. 3 | 4/C #10 | NOTE 4
1131 | C108 | A.C. POWER SUPPLY, AREA LT | JCT BOX No. 3 | AREA LIGHT No. 6 | 4/C #10 | NOTE 4
1132 | C100,C107 | A.C. POWER SUPPLY, AREA LT | JCT BOX No. 3 | JCT BOX No. 1 | 4/C #10 | NOTE 4
1133 | C101, C103 | A.C. POWER SUPPLY, AREA LT | JCT BOX No. 1 | AREA LIGHT No. 5 | 4/C #10 | NOTE 4
1134 | C107, C109 | A.C. POWER SUPPLY, AREA LT | JCT BOX No. 3 | JCT BOX No. 4 | 4/C #10 | NOTE 4
1135 | C110 | A.C. POWER SUPPLY, AREA LT | JCT BOX No. 4 | AREA LIGHT No. 7 | 4/C #10 | NOTE 4
1140 | C027, TRAY | ALARMS | XFMR SUMP PUMP ALARMS | SWITCHBOARD No. 1 | 4/C #10
1200 | TRAY | A.C. POWER SUPPLY | A.C. PANEL CKT. # 33/35 | DISC SWITCH, BATTERY CHARGER |  | BY BUILDING MANUFACTURER
1201 | TRAY | ALARMS | SWITCHBOARD No. 1 | BATTERY CHARGER No. 1 | 4/C #10
1202 | TRAY | D.C. POWER SUPPLY | D.C. PANEL CKT. # 33/35 | BATTERY CHARGER No. 1 |  | BY BUILDING MANUFACTURER
1203 | TRAY | D.C. POWER SUPPLY | D.C. PANEL MAIN | BATTERY BANK |  | BY BUILDING MANUFACTURER
1204 | TRAY | D.C. POWER SUPPLY | D.C. PANEL CKT. # 9/11 | SWITCHBOARD No. 1 | 2/C #10 | NOTE 5
1205 | TRAY | A.C. POWER SUPPLY | DISC SWITCH, BATTERY CHARGER | BATTERY CHARGER No. 2 |  | BY BUILDING MANUFACTURER
1206 | TRAY | ALARMS | SWITCHBOARD No. 1 | BATTERY CHARGER No. 2 | 4/C #10
1207 | TRAY | D.C. POWER SUPPLY | D.C. PANEL CKT. # 34/36 | BATTERY CHARGER No. 2 |  | BY BUILDING MANUFACTURER
1208 | TRAY | A.C. POWER SUPPLY | DISC SWITCH, BATTERY CHARGER | BATTERY CHARGER No. 1 |  | BY BUILDING MANUFACTURER
1211 | C200, TRAY | PACIFICORP INTERFACE | PACIFICORP INTERFACE CABINET | SWITCHBOARD No. 1 | 12/C #10
1212 | C201, TRAY | PACIFICORP INTERFACE | PACIFICORP INTERFACE CABINET | SWITCHBOARD No. 1 | 12/C #10
1231 | C204, TRAY | PACIFICORP METERING | PACIFICORP CONTROL HOUSE | SWITCHBOARD No. 1 | ADSS
1300 | C350, TRAY | STATION SERVICE | AUTO TRANSFER SWITCH No. 1 | LOCAL DISTRIBUTION POWER METER BREAKER | 3/C-3/0 SER w/ 1/0 GRD
1301 | C352 | LOCAL DISTRIBUTION STATION SERVICE | LOCAL DISTRIBUTION POWER METER BREAKER | LOCAL DISTRIBUTION UTILITY TRANSFORMER | 3/C-3/0 SER w/ 1/0 GRD
1406 | TRAY | H2 ALARM | HYDROGEN MONITOR | SWITCHBOARD No. 1 | 4/C #16
1408A | TRAY | DOUBLE DOOR ALARM | DOOR ALARM JUNCTION BOX | SWITCHBOARD No. 1 | 4/C #16
1408B | TRAY | SINGLE DOOR ALARM | DOOR ALARM JUNCTION BOX | SWITCHBOARD No. 1 | 4/C #16
1408C | TRAY | DOUBLE DOOR ALARM | DOOR ALARM JUNCTION BOX | SWITCHBOARD No. 1 | 4/C #16
1409 | TRAY | SMOKE DETECTOR | SMOKE DETECTOR | AC SUPPLY CKT. 41 |  | BY BUILDING MANUFACTURER
1410 | TRAY | SMOKE DETECTOR | SMOKE DETECTOR | SWITCHBOARD No. 1 | 4/C #16
3020 | TRAY | A.C. POWER SUPPLY | A.C. PANEL CKT. # 22 | BUILDING LIGHTS |  | BY BUILDING MANUFACTURER
3021 | TRAY | A.C. POWER SUPPLY | A.C. PANEL CKT. # 30 | BUILDING OUTLETS |  | BY BUILDING MANUFACTURER
3022 | TRAY | A.C. POWER SUPPLY | A.C. PANEL CKT. # 32 | BLDG EXHAUST FAN & H2 MONITOR |  | BY BUILDING MANUFACTURER
3025 | TRAY | A.C. POWER SUPPLY | A.C. PANEL CKT. # 37 | BUILDING FLOOD LIGHTS |  | BY BUILDING MANUFACTURER
3026 | TRAY | A.C. POWER SUPPLY | A.C. PANEL CKT. # 39 | BUILDING EXIT LIGHT |  | BY BUILDING MANUFACTURER
3027 | TRAY | A.C. POWER SUPPLY | A.C. PANEL CKT. # 43/45 | BUILDING HVAC |  | BY BUILDING MANUFACTURER
3240 | C261,TRAY | HV BUS POTENTIALS | HV BUS V.T. JUNCTION BOX NO. 2 | SWITCHBOARD NO.1 | 4/C #10 | NOTE 3
3242 | C259 | HV BUS POTENTIALS | HV BUS PHASE A P.T. | HV BUS V.T. JUNCT BOX NO. 2 | 2-1/C #10 | NOTE 3
3243 | C260 | HV BUS POTENTIALS | HV BUS PHASE B P.T. | HV BUS V.T. JUNCT BOX NO. 2 | 2-1/C #10 | NOTE 3
3244 | C262 | HV BUS POTENTIALS | HV BUS PHASE C P.T. | HV BUS V.T. JUNCT BOX NO. 2 | 2-1/C #10 | NOTE 3
3250 |  | IRIG | SAT CLOCK - OUT 1 | RTAC M8 - IRIG IN | COAXRG58 | BY OTHERS
3255 | TRAY | SAT CLOCK DOWNLEAD | SAT CLOCK M10 | TRAY-LIGHTNING ARRESTER | COAXRG6 | NOTE 8
3256 | TRAY | SAT CLOCK DOWNLEAD | CABLE TRAY - LIGHTNING ARRESTER | ANTENNA OUTSIDE HOUSE | COAXRG6 | NOTE 8
J11 |  | SCADA | PATCH PANEL No.1 (PP1) | RTAC | ZIP5FST | BY OTHERS
J12 |  | SCADA | PATCH PANEL No.1 (PP1) | RTAC | ZIP5FST | BY OTHERS
J13 |  | SCADA | PATCH PANEL No.1 (PP1) | RTAC | ZIP5FST | BY OTHERS
J14 |  | SCADA | PATCH PANEL No.1 (PP1) | RTAC | ZIP5FST | BY OTHERS
J18 |  | SCADA, PACIFICORP | PATCH PANEL No.1 (PP1) | RTAC | ZIP3S | BY OTHERS
J19 |  | SCADA | PATCH PANEL No.1 (PP1) | PV PLANT RTAC | MIC15M | BY OTHERS
J21 |  | SCADA | RTAC (SWITCHBOARD No. 1) | T1P (SWITCHBOARD No. 1) | EIA232 | BY OTHERS
J22 |  | SCADA | RTAC (SWITCHBOARD No. 1) | T1BU (SWITCHBOARD No. 1) | EIA232 | BY OTHERS
J23 |  | SCADA | RTAC (SWITCHBOARD No. 1) | T1 REV (SWITCHBOARD No. 1) | EIA232 | BY OTHERS
J24 |  | SCADA | 52T1 FIBER PATCH PANEL | ANNUN1 (PORT 3) | ZIP5MST | BY OTHERS
J25 |  | SCADA | F1 FIBER PATCH PANEL | F1 SEL 351S (PORT 2) | ZIP5MST | BY OTHERS
J30 |  | SCADA | T1 FIBER PATCH PANEL | ANNUN2 (PORT 3) | ZIP5MST | BY OTHERS
J31 |  | SCADA | T1 FIBER PATCH PANEL | ETM1 (PORT 2) | ZIP5MST | BY OTHERS
J32 | BUBBLES | SCADA | T1 FIBER PATCH PANEL | CAP1 (PORT 3) | EIA232 | BY OTHERS